## Sheet1
FILTRATION
DESCRIPTION | VALVES AND PUMPS | [24 empty] | STATUS
[8 empty] | FROM BW T | SERV W T |  |  |  | NAOCL DP V |  | HCL DP V |  |  |  | BW PUMPS |  |  |  | CHEM SPRINKLE |  | BLOWER
Filtration | EJ-ZS | AV-ZS | BW-ZS | SP-ZS | DR-ZS | FD-LV | FL-FV | FW-ZS-1 | SW-ZS-1 | AS-ZS-1 | BW-FV-1 | SP-FV-1 | CD-ZS-1 | CD-ZS-2 | CD-ZS-3 | CD-ZS-4 |  |  | BW-P1 | BW-P2 | BW-P3 | BW-P4 | CH-SP-1 | CH-SP-2 | AB1
Pass 1 | O | O | C | C | C | O% | C | C | C | C | C | C | C | C | C | C |  |  | C | C | C | C | C | C | C | FILLING
CHECK LEVEL 3.5 METERS
Pass 2 | O | O | C | C | C | O % | O @300 M3/H | C | C | C | C | C | C | C | C | C |  |  | C | C | C | C | C | C | C | FILTRATION
WAITING FOR 15 MINUTES
PASS 3 | C | C | C | C | C | O % | O @445M3/H | C | C | C | C | C | C | C | C | C |  |  | C | C | C | C | C | C | C
FILTRATIO TIME 2HOURS 45 MINUTES
CHECK IF ANOTHER CELL IN BW WAIT UNTIL THE BW COMPLETED
Pass 4 | C | C | C | C | C | C | O @445M3/H | C | C | C | C | C | C | C | C | C |  |  | C | C | C | C | C | C | C | PREPAIR BW
WAIT FOR 20 SEC CHECK LEVEL LESS THAN OR EQUAL TO 2.5 METERS
LEVEL LESS THAN OR EQUAL TO 2.5 YES GO TO PASS 6
LEVEL LESS THAN OR EQUAL TO 2.5 NO GO TO PASS 5
Pass 5 | C | C | C | C | O | C | O @445M3/H | C | C | C | C | C | C | C | C | C |  |  | C | C | C | C | C | C | C
CHECK LEVEL LESS THAN OR EQUAL TO 2.5 METERS DELAY 20 SECOND
Pass 6 | C | C | O | O | C | C | C | O | C | O | O @1300 M3/H | C | C | C | C | C |  |  | C | C | C | C | C | C | C | 1 ST BW
WAIT FOR 10SEC FOR VALVE FB
Pass 7 | C | C | O | O | C | C | C | O | C | O | O @1300 M3/H | C | C | C | C | C |  |  | O |  |  | C | C | C | O
BW TIME 35 SECOND
Pass 8 | C | C | O | O | O | C | C | O | C | O | O @1300 M3/H | C | C | C | C | C |  |  | C | C | C | C | C | C | O | INITIAL DRAIN
LEVEL LESS THAN OR EQUAL 0.2 METERS
Pass 9 | C | C | O | O | O | C | C | O | C | O | O @1300 M3/H | C | C | C | C | C |  |  | C | C | C | C | C | C | C
DELAY 10 S
Pass 10 | C | C | O | O | O | C | C | O | C | O | O @1300 M3/H | O @600 M3/H | C | C | C | C |  |  | C | C | C | C | C | C | C | 2 ND BW
DELAY 10 S
Pass 11 | C | C | O | O | O | C | C | O | C | C | O @1300 M3/H | O @600 M3/H | C | C | C | C |  |  | O |  |  |  | C | C | C
DELAY 35 S
Pass 12 | C | C | O | O | O | C | C | O | C | C | O @1300 M3/H | O @600 M3/H | C | C | C | C |  |  | O | C | C | C | C | C | C | FINA FLUSHING
DELAY10S
Pass 13 | C | C | O | O | O | C | C | O | C | C | C | O @600 M3/H | C | C | C | C |  |  | O | C | C | C | C | C | C
DELAY35S
Pass 14 | C | C | O | O | O | C | C | O | C | C | C | O @600 M3/H | C | C | C | C |  |  | C | C | C | C | C | C | C
CHECK LEVEL<=0M
Pass 15 | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C |  |  | C | C | C | C | C | C | C
START SECOND FILTRATION
NAOCL CEB
DESCRIPTION | VALVES AND PUMPS | [24 empty] | STATUS
[8 empty] | FROM BW T | SERV W T |  |  |  | NAOCL DP V |  | HCL DP V |  | NAOCL DP | HCL DP | BW PUMPS |  |  |  | CHEM SPRINKLE |  | BLOWER
CEB NAOCL | EJ-ZS | AV-ZS | BW-ZS | SP-ZS | DR-ZS | FD-LV | FL-FV | FW-ZS-1 | SW-ZS-1 | AS-ZS-1 | BW-FV-1 | SP-FV-1 | CD-ZS-1 | CD-ZS-2 | CD-ZS-3 | CD-ZS-4 | CDP-10,11 | CDP-12,13 | BW-P1 | BW-P2 | BW-P3 | BW-P4 | CH-SP-1 | CH-SP-2 | AB1
Pass 1 | C | C | O | O | C | C | C | O | C | O | O @1300 M3/H | C | C | C | C | C |  |  | C | C | C | C | C | C | C | FILLING
WAIT 10 S
Pass 2 | C | C | O | O | C | C | C | O | C | O | O @1300 M3/H | C | C | C | C | C | C | C | O |  |  | C | C | C | C | BW DOSING
CHECK LEVEL>=1.25 METERS
PASS 3 | C | C | O | O | C | C | C | O | C | O | O @200 M3/H | C | O | C | C | C | C | C | O | C | C | C | C | C | C
WAIT 10 SECOND
Pass 4 | C | C | O | O | C | C | C | O | C | O | O @200 M3/H | C | O | C | C | C | O | C | O | C | C | C | C | C | C
WAIT FOR 3 MINUTES AND LEVEL MUST BE 2.3 METERS
Pass 5 | C | C | O | O | C | C | C | O | C | O | O @200 M3/H | C | O | C | C | C | C | C | C | C | C | C | C | C | C | SOCKING
WAIT 10 SECOND
Pass 6 | C | C | O | O | C | C | C | O | C | O | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C
WAIT FOE 2 MINUTES
Pass 7 | C | C | O | O | C | C | C | O | C | O | C | C | C | C | C | C | C | C | C | C | C | C | C | C | O
BLOWER START FOR 30 SECOND
Pass 8 | C | C | O | O | O | C | C | O | C | O | O @1300 M3/H | O @600 M3/H | C | C | C | C | C | C | C | C | C | C | C | C | C | RINSING
WAIT FOR 10 SECOND
Pass 9 | C | C | O | O | O | C | C | O | C | O | O @1300 M3/H | O @600 M3/H | C | C | C | C | C | C | O |  |  |  | C | C | C
DELAY35 S
Pass 10 | C | C | O | O | O | C | C | O | C | O | O @1300 M3/H | O @600 M3/H | C | C | C | C | C | C | O | C | C | C | C | C | C | FINAL FLUSHING
DELAY 10 S
Pass 11 | C | C | O | O | O | C | C | O | C | O | C | O @600 M3/H | C | C | C | C | C | C | O | C | C | C | C | C | C
DELAY 30 S
Pass 12 | C | C | O | O | O | C | C | O | C | C | C | O @600 M3/H | C | C | C | C | C | C | C | C | C | C | C | C | C
DELAY 10 S
Pass 12 | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C
START HCL CEB
HCL CEB
DESCRIPTION | VALVES AND PUMPS | [24 empty] | STATUS
[8 empty] | FROM BW T | SERV W T |  |  |  | NAOCL DP V |  | HCL DP V |  | NAOCL DP | HCL DP | BW PUMPS |  |  |  | CHEM SPRINKLE |  | BLOWER
HCL CEB | EJ-ZS | AV-ZS | BW-ZS | SP-ZS | DR-ZS | FD-LV | FL-FV | FW-ZS-1 | SW-ZS-1 | AS-ZS-1 | BW-FV-1 | SP-FV-1 | CD-ZS-1 | CD-ZS-2 | CD-ZS-3 | CD-ZS-4 | CDP-10,11 | CDP-12,13 | BW-P1 | BW-P2 | BW-P3 | BW-P4 | CH-SP-1 | CH-SP-2 | AB1
Pass 1 | C | C | O | O | C | C | C | O | C | O | O @1300 M3/H | C | C | C | C | C |  |  | C | C | C | C | C | C | C | FILLING
WAIT 10 S
Pass 2 | C | C | O | O | C | C | C | O | C | O | O @1300 M3/H | C | C | C | C | C | C | C | O |  |  | C | C | C | C | BW DOSING
CHECK LEVEL>=1.25 METERS
PASS 3 | C | C | O | O | C | C | C | O | C | O | O @200 M3/H | C | C | C | O | C | C | C | O | C | C | C | C | C | C
WAIT 10 SECOND
Pass 4 | C | C | O | O | C | C | C | O | C | O | O @200 M3/H | C | C | C | O | C | C | O | O | C | C | C | C | C | C
WAIT FOR 3 MINUTES AND LEVEL MUST BE 2.3 METERS
Pass 5 | C | C | O | O | C | C | C | O | C | O | O @200 M3/H | C | C | C | O | C | C | C | C | C | C | C | C | C | C | SOCKING
WAIT 10 SECOND
Pass 6 | C | C | O | O | C | C | C | O | C | O | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C
WAIT FOR 120 SECOND SOCKING TIME
Pass 7 | C | C | O | O | C | C | C | O | C | O | C | C | C | C | C | C | C | C | C | C | C | C | C | C | O
BLOWER START FOR 30 SECOND
Pass 8 | C | C | O | O | O | C | C | O | C | O | O @1300 M3/H | O @600 M3/H | C | C | C | C | C | C | C | C | C | C | C | C | C | RINSING
WAIT FOR 10 SECOND
Pass 9 | C | C | O | O | O | C | C | O | C | O | O @1300 M3/H | O @600 M3/H | C | C | C | C | C | C | O |  |  |  | C | C | C
DELAY30 S
Pass 10 | C | C | O | O | O | C | C | O | C | O | O @1300 M3/H | O @600 M3/H | C | C | C | C | C | C | O | C | C | C | C | C | C | FINAL FLUSHING
DELAY 10 S
Pass 11 | C | C | O | O | O | C | C | O | C | O | C | O @600 M3/H | C | C | C | C | C | C | O | C | C | C | C | C | C
DELAY 30 S
Pass 12 | C | C | O | O | O | C | C | O | C | C | C | O @600 M3/H | C | C | C | C | C | C | C | C | C | C | C | C | C
DELAY 10 S
Pass 12 | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C
START FILTRATION
CIP NAOCL
DESCRIPTION | VALVES AND PUMPS | [24 empty] | STATUS
[8 empty] | FROM BW T | SERV W T |  |  |  | NAOCL DP V |  | HCL DP V |  | NAOCL DP | HCL DP | BW PUMPS |  |  |  | CHEM SPRINKLE |  | BLOWER
HCL NAOCL | EJ-ZS | AV-ZS | BW-ZS | SP-ZS | DR-ZS | FD-LV | FL-FV | FW-ZS-1 | SW-ZS-1 | AS-ZS-1 | BW-FV-1 | SP-FV-1 | CD-ZS-1 | CD-ZS-2 | CD-ZS-3 | CD-ZS-4 | CDP-10,11 | CDP-12,13 | BW-P1 | BW-P2 | BW-P3 | BW-P4 | CSP-O1 | CSP--2 | AB1
Pass 1 | C | C | O | C | C | C | C | C | C | O | O @100% | O @100% | O | C | C | C |  |  | C | C | C | C | C | C | C | DOSING
DELAY FOR 10 S
PASS 2 | C | C | O | C | C | C | C | C | C | O | O @100% | O @100% | O | C | C | C | O |  | C | C | C | C | O @35 HZ | C | C
CHECK LEVEL>=2.3 METERS
Pass 3 | C | C | O | C | C | C | C | C | C | O | O @100% | O @100% | C | C | C | C | C |  | C | C | C | C | C | C | C | SOCKING
WAIT FOR 1 HOUR
Pass 4 | C | C | O | O | C | C | C | O | C | O | O @1300 M3/H | O @600 M3/H | C | C | C | C | C |  | C | C | C | C | C | C | C | RINSING
WAIT 10 SECOND
Pass 5 | C | C | O | O | C | C | C | O | C | O | O @1300 M3/H | O @600 M3/H | C | C | C | C | C |  | O |  |  | C | C | C | O
WAITING FOR 35 SECOND
Pass 6 | C | C | O | O | O | C | C | O | C | O | O @1300 M3/H | O @600 M3/H | C | C | C | C | C |  | O | C | C | C | C | C | O
WAITING FOR 10 SECOND
Pass 7 | C | C | O | O | O | C | C | O | C | O | C | O @600 M3/H | C | C | C | C | C |  | O | C | C | C | C | C | O | RINSING
WAIT FOR 35 SECOND
Pass 8 | C | C | O | O | O | C | C | O | C | O | C | O @600 M3/H | C | C | C | C | C |  | C | C | C | C | C | C | O
CHECK LEVEL< 0.2 METERS
Pass 9 | C | C | O | O | O | C | C | O | C | O | C | O @600 M3/H | C | C | C | C | C |  | C | C | C | C | C | C | C | FINAL FLUSHING
LEVEL 0
Pass 10 | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C |  | C | C | C | C | C | C | C
START FILTRATION
CIP HCL
DESCRIPTION | VALVES AND PUMPS | [24 empty] | STATUS
[8 empty] | FROM BW T | SERV W T |  |  |  | NAOCL DP V |  | HCL DP V |  | NAOCL DP | HCL DP | BW PUMPS |  |  |  | CHEM SPRINKLE |  | BLOWER
HCL NAOCL | EJ-ZS | AV-ZS | BW-ZS | SP-ZS | DR-ZS | FD-LV | FL-FV | FW-ZS-1 | SW-ZS-1 | AS-ZS-1 | BW-FV-1 | SP-FV-1 | CD-ZS-1 | CD-ZS-2 | CD-ZS-3 | CD-ZS-4 | CDP-10,11 | CDP-12,13 | BW-P1 | BW-P2 | BW-P3 | BW-P4 | CSP-O1 | CSP--2 | AB1
Pass 1 | C | C | O | C | C | C | C | C | C | O | O @100% | O @100% | C | C | O | C |  |  | C | C | C | C | C | C | C | DOSING
DELAY FOR 10 S
PASS 2 | C | C | O | C | C | C | C | C | C | O | O @100% | O @100% | C | C | O | C | C | O | C | C | C | C | O @35 HZ | C | C
CHECK LEVEL>=2.3 METERS
Pass 3 | C | C | O | C | C | C | C | C | C | O | O @100% | O @100% | C | C | C | C | C |  | C | C | C | C | C | C | C | SOCKING
WAIT FOR 1 HOUR
Pass 4 | C | C | O | O | C | C | C | O | C | O | O @1300 M3/H | O @600 M3/H | C | C | C | C | C |  | C | C | C | C | C | C | C | RINSING
WAIT 10 SECOND
Pass 5 | C | C | O | O | C | C | C | O | C | O | O @1300 M3/H | O @600 M3/H | C | C | C | C | C |  | O |  |  | C | C | C | O
WAITING FOR 35 SECOND
Pass 6 | C | C | O | O | O | C | C | O | C | O | O @1300 M3/H | O @600 M3/H | C | C | C | C | C |  | O | C | C | C | C | C | O
WAITING FOR 10 SECOND
Pass 7 | C | C | O | O | O | C | C | O | C | O | C | O @600 M3/H | C | C | C | C | C |  | O | C | C | C | C | C | O | RINSING
WAIT FOR 35 SECOND
Pass 8 | C | C | O | O | O | C | C | O | C | O | C | O @600 M3/H | C | C | C | C | C |  | C | C | C | C | C | C | O
CHECK LEVEL< 0.2 METERS
Pass 9 | C | C | O | O | O | C | C | O | C | O | C | O @600 M3/H | C | C | C | C | C |  | C | C | C | C | C | C | C | FINAL FLUSHING
LEVEL 0
Pass 10 | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C |  | C | C | C | C | C | C | C
START FILTRATION